## AV-new
TEST REPORT
CUSTOMER NAME |  |  | Pin Point Engineers
ADDRESS |  |  | Dehradun
NAME OF TEST |  |  | PAO REPORT
TEST TAKEN ON |  |  | 12/04/2023
AHU NO. |  |  | AHU NUMBER
LOCATION |  |  | Demo Department Pao
REPORT NO. |  |  | PPE003PAO120420231
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  | SR.NO. |  | VALIDITY
Photometer |  | PH-5 |  |  | 2829 |  | 16/01/2024
OBSERVATIONS:
Room Name & ID No. | Inlet No. |  | Upstream Conc (μg/l) |  | Leakage Found (%) | Remark
ROOM NUMBER | 123 |  | 70 |  | 0.00001 | Pass
Compressed Air Pressure 123 kg/cm²
Acceptance criteria :Leakage should not be more Than 0.01 %
REPORT PREPARED BY |  |  |  | VERIFIED BY
PIN POINT ENGINEERS |  |  |  | Pin Point Engineers
Report Prepared by tempus64