## AV-new
TEST REPORT
CUSTOMER NAME |  |  | Pin Point Engineers
ADDRESS |  |  | Dehradun
NAME OF TEST |  |  | PAO REPORT
TEST TAKEN ON |  |  | 13/05/2023
AHU NO/EQUIPMENT ID |  |  | 5
LOCATION |  |  | mklj
REPORT NO. |  |  | PPE003PAO130520231
STANDARD INSTRUMENT USED FOR TEST:
INSTRUMENT NAME |  | MAKE/MODEL |  |  | SR.NO. |  | VALIDITY
Photometer |  | PH-5 |  |  | 2829 |  | 16/01/2024
OBSERVATIONS:
Room Name/ /Equipment Name | Inlet No. |  | Upstream Conc (μg/l) |  | Leakage Found (%) | Remark
iojjk | ihhu |  | 68 |  | 0.0015 | Pass
| ihhu |  | 90 |  | 0.203 | Fail
| ihhu |  | 50 |  | 0.0101 | Fail
| ihhu |  | 24 |  | 0.0024 | Pass
Compressed Air Pressure 21 kg/cm²
Acceptance criteria :Leakage should not be more Than 0.01 %
REPORT PREPARED BY |  |  |  | VERIFIED BY
PIN POINT ENGINEERS |  |  |  | Pin Point Engineers
Report Prepared by tempus64